## Slide 1
Topic : Network Modelling

## Slide 2
COPYRIGHT NOTICE
All rights reserved. This entire publication is subject to the laws of copyright. This publication is confidential and sole property of EirGrid plc and SONI Limited. No part of this publication may be reproduced or transmitted in any form or by any means, electronic or manual, including photocopying without the prior written permission of EirGrid plc and SONI Limited. © SONI Limited / EirGrid Plc 2019
DOCUMENT DISCLAIMER
This manual is intended as a guide only. Whilst every effort is made to provide information that is useful, and care is taken in the preparation of the information, EirGrid plc and SONI limited give no warranties or representations, expressed or implied, of any kind with respect to the contents of this document, including, without limitation, its quality, accuracy and completeness. EirGrid plc and SONI limited hereby exclude, to the fullest extent permitted by law, all and any liability for any loss or damage howsoever arising from the use of this document or any reliance on the information it contains. Use of this document and the information it contains is at the user’s sole risk.

## Slide 3
Presentation Overview
Securing the system against thermal overloads
Function and operation of the Network Security Monitor (NSM) in the scheduling and dispatch process.
Interaction of NSM constraints with other constraints and a regional look at constraint issues.

## Slide 4
System Security & Thermal Limits
The control centres are responsible for securing the system in real time in accordance with the Security Standards including respecting thermal limits.
Each transmission line and transformer has a rated current which must not be exceeded.
High current could lead to thermal damage to equipment or excessive sagging threatening the power system or public safety.

## Slide 5
System Security & Thermal Limits
In general CHCC/ NCC can’t directly change the flow on a individual line.
Rebalancing of supply will ultimately be needed (although this will often be subsumed by the general task of matching supply and demand)
Redispatch is done on the basis of minimising the cost of deviation from PNs while ensuring system security and respecting priority dispatch.
The main remedial action is to redispatch generation which is contributing to the problem. This will usually impact flows across multiple lines.

## Slide 6
System Security & Thermal Limits
The Security Standards specify that ratings may not be exceeded for N-1 contingency events. For the loss of any single piece of transmission equipment, the resultant flows must observe limits.
A note on ratings: Limits vary seasonally – equipment ratings are higher in colder months due to a lower average ambient temperatures
N-1 is the industry standard and ensures that cascade trippings don’t bring down large portions of the system

## Slide 7
Network Security Monitor
The Network Security Monitor uses a mathematical model of the power system. It specifies the electrical properties of each element and how these elements are configured.
In real time possible remedial actions may be more limited or not possible and so analysis in the scheduling timeframe required.
New for ISEM is the incorporation of a Network Security Monitor into the Scheduling and Dispatch process. This aims to ensure that the schedule meets security standards for each interval.

## Slide 8
Network Security Monitor
The Inputs
  Scheduled generator outputs
  Forecast demand at each distribution node
The Outputs
  The current flowing on each circuit or transformer compared against the rated value.
For N-1 analysis
  Each circuit element is removed in-turn, resulting in hundreds of powerflow studies.
This process is automated and repeated for each scheduling interval. (30 min for LTS, 15 min for RTC and 5 min for RTD)

## Slide 9
Network Security Monitor
NSM
NCUC
This whole process iterates between the Unit Commitment solver (NCUC) and NSM.
NCUC determines an initial schedule based on PNs, commercial and technical offer data, constraints etc.
Using this schedule NSM performs N-1 powerflow analysis

## Slide 10
Network Security Monitor
NSM
NCUC
Any violations are reported back to NSM along with associated ‘Shift Factors’ – i.e. the contributory factor for each generator and associated penalty cost.
NCUC reruns using the new information.
NSM reruns using the new schedule.
The process will iterate until a secure schedule is determined

## Slide 11
Simple Example
X =
150MW
Y =
200MW
Z =
OFF
10% Overload of 20 MW on Line A
Initial NCUC schedule for 3 unit system for scheduling interval 13:30 to 14:00. Long notice unit Z is OFF.
 | 13:30 – 14:00
X | 150 MW
Y | 200 MW
Z | OFF
NSM determines that the schedule will cause overloads on Line A. ‘Shift Factor’ for all units passed back to NCUC.

## Slide 12
Simple Example
X =
140MW
Y =
160MW
Z =
50 MW
No Overload on Line A
NCUC now moves Units X and Y down according to their COD and TOD. Unit Z will now be committed.
 | 13:30 – 14:00
X | 140 MW
Y | 160 MW
Z | 50 MW
NSM rechecks the schedule. Overload on Line A is resolved.
Note that in this example 50 MW of generation had to be constrained to resolve a 20 MW overload. This is due to the meshed nature of the Transmission System.

## Slide 13
Network Security Monitor
The Network Model is kept in tight alignment with the primary Energy Management System model used by the Control Rooms.
Both models are updated every three weeks to account for physical changes to the system.
The current operational configuration is then layered on top of this default network model as follows:
LTS
Default Network Model
+ Planned Outages
+ Planned Operational Switching
RTC & RTD
Default Network Model
+ Live System Information

## Slide 14
Network Security Monitor
The Network Security Model utilises a simplified DC loadflow approximation. Analysis is limited to Thermal/ Overload issues.
In addition weekly lookahead constraint studies are performed for selected regions and are used as an input for the Unit Commitment solver. Thermal violations are examined but voltage, short circuit and transient issues can also be identified at this stage.
Weekly constraint studies are performed for assumed system conditions. As a result outputs are widened to allow the Network Security Model to act as primary tool for determining thermal constraints.
Weekly constraint studies are subject to ongoing review for revision in light of the development of new tools e.g. lookahead WSAT, voltage trajectory tool etc.

## Slide 15
Specific Network Issues – South West/ West
Constraints in SW currently driven by:
  Projects to reconfigure the stations at Moneypoint and Kilpaddoge and associated outages.
  220kV Line uprates between Kilpaddogge and Knockraha and associated outages.
  In 2019 – Forced outage of Moneypoint T4201. An important link between the 400kV and 220kV network. (Due to be resolved following transfer of T4202 in late October)
  General West to East constraints across the country exist as well as more local constraints.

## Slide 16
Constraint exists in Cork Harbour for an intact Network and are compounded during 220kV or 110kV outages.
Specific Network Issues – Cork
Possibility constraints may be alleviated somewhat by reconfiguration of Aghada 220kV Substation
Significant works planned for Knockraha 220kV Substation 2020 to 2022. Large duration 220kV outages anticipated.

## Slide 17
Specific Network Issues – South East
Station uprate projects in Wexford and Kilkenny driving constraints.
Generally not heavily constrained for intact network.

## Slide 18
Constraints common in Donegal and NW particularly during outages.
Specific Network Issues - Northwest
Periods of low load generally worse as more wind generation needs to be exported from the region.
Specific constraint boundary south of Clogher 110kV managed through CRU defined Donegal constraint group.

## Slide 19
West to East constraints generally seen during 110kV outages.
Specific Network Issues – Northern Ireland
Level of constraints affected by running of CCGT in the west.
During certain weather warnings Coolkeeragh Magherfelt 275kV double circuit treated as single N-1 contingency. System operated more defensively.

## Slide 20: Questions