## Slide 1
System Constraints

## Slide 2
COPYRIGHT NOTICE
All rights reserved. This entire publication is subject to the laws of copyright. This publication is confidential and sole property of EirGrid plc and SONI Limited. No part of this publication may be reproduced or transmitted in any form or by any means, electronic or manual, including photocopying without the prior written permission of EirGrid plc and SONI Limited. © SONI Limited / EirGrid Plc 2019
DOCUMENT DISCLAIMER
This manual is intended as a guide only. Whilst every effort is made to provide information that is useful, and care is taken in the preparation of the information, EirGrid plc and SONI limited give no warranties or representations, expressed or implied, of any kind with respect to the contents of this document, including, without limitation, its quality, accuracy and completeness. EirGrid plc and SONI limited hereby exclude, to the fullest extent permitted by law, all and any liability for any loss or damage howsoever arising from the use of this document or any reliance on the information it contains. Use of this document and the information it contains is at the user’s sole risk.

## Slide 3
SEM
Market Schedule
Operational Schedule
ISEM
Balancing Market Schedules
SEM to ISEM
Now system constraints that were considered as part of operational schedule are part of the Market Schedule

## Slide 4
Updated monthly with longer term changes due to transmission upgrades or policy updates
Updated on weekly basis with changes to constraints that vary due the outage program
Operational Constraints

## Slide 5: Overview of Constraint Types

## Slide 6
Inter Area flow modelling in scheduling tools

## Slide 7: North-South Inter Area Flow
Generators increase their output providing reserve in response to a tripping on the system.
Scheduling tool takes into account the flow that occurs after a tripping – A tripping would increase the flow in a particular direction across the “Tie-Line”
Max Limit North to South on Tie Line is 450MW (actual + rescue) which is linked to the Largest Single infeed in each jurisdiction
Generator trip in ROI
Info note on Inter Area Flow

## Slide 9
Power
Heavy metal shaft of spinning turbine connected to electrical generator – High Inertia
Generator Transformer
Same frequency as house supply
3000rpm = 50Hz
Inertia and Rate of Change of frequency
3000rpm = 50 Hz

## Slide 10
ROCOF – Rate of change of Frequency. Limited to 0.5Hz/s
Lower Inertia System

## Slide 11: Non Synchronous Generation
Units connected through a power converter are not counted as Synchronous (including Interconnectors Moyle and EWIC)
Inertia
ROCOF
SNSP
Additional metric to limit amount of non synchronous plant
Non Synchronous

## Slide 12: System Stability Constraints

## Slide 13: Jurisdictional Constraints – System Stability
Grid Frequency – No oscillations
Power Stability
Rotor Angle - Generators
Voltage Stability
Dynamic/transient studies looking at millisecond responses across power system

## Slide 14
Grid Frequency - Oscillation on Power System
Oscillation of ~ 0.3Hz - This equates to about 150MW

## Slide 15
Voltage Instability in Donegal
16:30
Healthy 110kV voltages ~113kV
Sudden voltage degradation as Load increases suddenly – Capacitor switched in to increase voltage and avoid cascading voltage collapse
102kV

## Slide 16
Reserves
Chapter 2 in Operational Constraints

## Slide 17: Reserve – replace lost power
N-1 secure – Loss of any single element/Generator
Concept of Largest Single infeed(outfeed)
75% of the largest single infeed is covered
New System service products

## Slide 19
Replacement Reserve
325MW spare capacity on fast acting plant
125MW required in NI
450MW Total all island to cover largest loss

## Slide 20
Negative Reserve
Traditionally held to deal with scenario where generators are at min gen and the system load is lower than forecast (frequency moves > 50Hz)
Interconnection and wind forecast error also feed into this
Can interact with other constraints( requirement overnight to hold primary reserve ) – some generators need to be above min to provide reserve

## Slide 21: Illustration of Reserve Curve
Defect

## Slide 22
Constraints binding when?
Constraint Type | Operational Constraint is Binding if … | Unit is Bound by this Constraint if …
Inertia | <= Limit | Provides inertia and is at LOL
SNSP | = Limit | Wind < HOL, IC < HOL, TH pumping
RoCoF | = Limit | Loss would lead to the RoCoF limit
MW | <= Min Limit >= Max Limit | As per constraint
MWR | >= Limit | All units in jurisdiction that is exporting power. There are exceptions to this.
NB | <= Min Limit >= Max Limit | At LOL
Reserves | = Limit | Is at a point in its reserve curve where a change in output would reduce provision
Determining System Operator and Non Marginal Flags

## Slide 23
Thermal only
DC Load flow ( doesn’t capture voltage issues)
Per scheduling interval over study horizon with relevant inputs (outages etc)
Network model in Scheduling Tool
Entire week of outages studied
Low/High Wind
Varying demand
Exports/Imports
Weekly Constraints
Underlying constraints on network or global system constraints that can arise on intact network
Looks at all types of constraints (voltage, thermal, security)
Monthly Operational Constraints
Operationally cannot create explicit constraints for every thermal contingency as the constraint may arise only for a short period
Any longer term recurring constraints will added to the scheduling system