## Slide 1: Metering Modification to T&S code
Cathal Kearney
Protection & Metering
03/12/2015

## Slide 2: Outline
SEM Mod_4_15 raised at the April 2015 meeting 61
Meter Operator to liaise with Proposer in relation to cost / benefit analysis of implementation of proposal
Presentation on issue to IWEA at Tripartite meeting in May
ESBN / EirGrid and SEM-O investigated impact on Market and options to resolve issue
Investigation and Options outlined to CER

## Slide 3: Joint investigation
ESBN MO and EirGrid MDP investigated impact in relation to loss of meter data to SEM
Greater numbers of DSO connected Generation Units changing to Price effecting over the last 2 years
Identified that communication and loss of power supply to DSO meters impact on MDP and SEM requirement for Settlement
Developed options and costs to resolve meter power supply and communications issues

## Slide 4: Solutions identified
DSO customers to provide robust communication channels, this option does not tackle loss of power supply to energy meters but would reduce communication problems only. Requirement is covered by DSO connection agreement.
Option – Installation of meter data logger with back up power supply and communication support – Minimum standard to allow MDP to poll meter data, approx. cost €4000 per metering point and on-going ESBN O&M charges would need to be reviewed – Retro fit option for existing DSO connected customers only (does not include telecom lines).
Option – Installation of DSO energy meter & communications to current TSO equivalent standard (energy meters with back up power supply and robust communication channels). Approx. additional cost of €15,000 per metering point and on-going ESBN O&M charges would need to be reviewed. This would be an option for existing connections and would become the standard for new DSO connections

## Slide 5: Summary
CER noted issue has arisen and to write to EirGrid and ESBN in relation to working together to resolve the issue
ESBN and EirGrid to develop coordinated approach to communicating with affected parties in the coming weeks, this would mean that
  Current DSO connections wishing to change to Price Effecting metering requirements will need to meet TSO equivalent standards as part of registration (See previous options)
  Where existing DSO Price effecting units are causing issues metering requirements will need to be fulfilled (See previous options)
Provision 3.77 in the T&SC for MDP to inform the Market Operator if a unit does not fulfil its metering requirements for the classification requested.
Roles and responsibilities in relation to MDP and MO roles to be explored in the Metering Group forum for I-SEM
Proposer requests that SEM Mod_4_15 MODIFICATION TO RELEVANT METER OPERATOR ROLE AND SUPPORT REQUIREMENTS FOR METER COMMUNICATION CHANNELS - is deferred until this process is finalised