## Slide 1
Mod_18_10 Intra Day Trading Working Group 4
  SO Impact Assesment

## Slide 2: Impact Assessment of Option Group 1
Security Issues
Notes: <number>

## Slide 3: Security Issues – Some Facts
 | Ireland |  | GB | 
Max. Demand | 6,700 MW |  | 60,000 MW | 
Installed Wind | 3,100 | 46% | 10,000 | 17%
Interconnector Capacity | 1000 MW | 15% | 4,000 MW | 7%
Largest Generation Infeed | 445 MW | 7% | 1,320 MW | 2%
Impact Assessment of Option Group 1
Comparison of forecast system capacities in 2013/14:

## Slide 4: Security Issues – Some Facts
Relative to other power systems, the all Island power system:
  has large generation unit sizes,
  has a high level of variable wind penetration which will grow further,
  will have significant external interconnection capacity,
These factors increase the criticality of unit commitment decisions:
  Over committing will lead to an increase in constraint costs.
  Under committing will lead to load shedding.
Impact Assessment of Option Group 1

## Slide 5: Security Issues - Potential Interconnector Flow Changes
Moyle Interconnector capacity at present is restricted to 450 MW import to 80 MW export with a rate of change limit of 300 MW/Trading Period (10 MW/min).
  Represents a potential 530 MW swing in < 1 hour.
Post EWIC, Interconnector capacity will be to 950 MW import to 580 MW export (assuming application of same 10 MW/min loading restriction).
  Represents a possible 1530 MW swing in < 2.6 hours.
If Moyle capacity increases to +/- 500 MW the flow limits become -1000 / +1000 MW (assuming application of same 10 MW/min loading restriction).
  Represents a possible 2000 MW swing in < 3.4 hours.
Impact Assessment of Option Group 1

## Slide 6: Security Issues - Generator Notice Times and Gate Closure
The notice time required to synchronise a generator and get it up to minimum load can be up to 18 hours.
The market software does not take into account these notice times and will transition a unit from zero to minimum load in one trading period.
As gate closure and setting of the Moyle schedule occur approximately 18 hours before the start of the trading day, unit commitment decisions can currently be managed by the TSOs to minimise any security issues although constraint costs do arise.
Additional market gate openings between D-1, the start of the trading day and within the trading day will result in shorter notice time for plant commitment changes.
Impact Assessment of Option Group 1

## Slide 7: Security Issues - Generator Notice Times and Gate Closure
Impact Assessment of Option Group 1

## Slide 8: Security Issues – Impacts
The system generation requirement to meet a possible 1530 MW interconnector flow change with increasing system load and decreasing wind generation describes a boundary for security consideration.
The magnitude of potential interconnector flow changes from export to import will require plant to be de-synchronised, this situation also requires consideration in terms of plant minimum on times, minimum down times (for re-synchronising when required) and two shifting limitations.
Market schedules that are prepared closer to real time may not be physically realisable as plant which has to be run up from cold or warm may not be available in time – this could result in insufficient generation to meet demand and exports.
Under extreme situations where NI generation is capacity limited, the N/S tie-line is constrained and SO-SO trades are unavailable due to GB generation unavailability , SONI could be required to load shed customers and maintain an export to GB.
Impact Assessment of Option Group 1

## Slide 9: Security Issues – Summary
The magnitude and rate of interconnector flow changes coupled with a reduction in the time available to schedule plant has the potential to adversely affect system security.
Mitigation tools need to be developed to ensure system security is maintained.
Mitigation of security issues will lead to changes in constraint costs (and potentially other non market costs) which need to be considered.
Impact Assessment of Option Group 1

## Slide 10: Impact Assessment of Option Group 1
Mitigation Options
Notes: <number>

## Slide 11: Security – Mitigation options
The following possible Security Mitigations could be adopted to manage security issues:
  1. Market scheduling
    The market scheduling engine modified to reflect generator parameters more accurately
      Generation plant notice times
      Generation run up characteristics
    Market Optimisation time horizons need to be considered to ensure the period does not finish prior to peak demands
      Consider optimisation time period length extension
      Consider optimisation start boundary information requirements
Impact Assessment of Option Group 1

## Slide 12: Security – Mitigation Options
  2. Interconnector ramp rates
    The introduction of another interconnector requires consideration of ramp rate limits for normal operation and as a security mitigation control to limit excessive TP to TP changes.
    The reduction of the interconnector ramp rates to mitigate security issues would reduce the ramp rate to very small values which would restrict trading during normal operation.
  3. Constraining interconnector flows for security
    If required for security the interconnector flows could be dispatched in a similar manner to generation, i.e. DQ ≠ MIUN
    How would this be managed from a trader perspective i.e. closing out positions?
Impact Assessment of Option Group 1

## Slide 13: Security – Mitigation Options
  4. ATC changes
    A reduction in transfer capacity applied for security reasons in a similar manner to the GB / French interconnector rules
  5. Generator Flexibility Incentives
    e.g. introduce ‘warming’ contracts to shorten notice times.
  6. SO-SO trades (already in place but not always available)
Impact Assessment of Option Group 1

## Slide 14
    Security mitigation
    Control the issue by producing market interconnector schedules that can be physically accommodated without compromising system security.
    Allow alteration of the schedule by the SO to maintain security. Prior to altering an interconnector scheduled flow the SO would, after normal plant scheduling, trade out of the situation, if trades are not available then the transfer would be restricted by either by an ATC reduction or dispatch constraint.
Impact Assessment of Option Group 1

## Slide 15
The following example of Market and RCUC run timings have been produced for option 1 assuming:
Both Generation and Interconnector users will bid at gate openings
RCUC can handle more than one price per trading day
The market produces an interconnector schedule that does not require alteration for security
Impact Assessment of Option Group 1

## Slide 16
Option 1 – an additional gate closure before the start of the trading day and
another after the start of the trading day.
The chart overleaf indicates an example of gate and RCUC run timings
The chart is split in two, the top section indicates market gate closures
and market scheduling runs. The bottom section indicates RCUC runs.
After a market schedule run finishes the market Interconnector schedule is
produced, published to participants and made available to the SO
for a RCUC run. The length of time required for RCUC runs is dependant
on the duration being scheduled and the likelihood of requiring multiple iterations.
The numbers at the start of each RCUC run indicate the starting data source
from previous completed RCUC runs, also numbered.
Impact Assessment of Option Group 1

## Slide 17
Impact Assessment of Option Group 1
Example of Gate Closure and RCUC Run Timings
Notes: <number>

## Slide 18
Constraints
  Difficult to model constraints impact, could be significant but no quantitative figure available
Resource
  Resources required for additional RCUC runs
  Working arrangements to be altered in the support staff e.g. extended working day till 23.00 and additional control room staff/3rd desk in the control rooms
IT systems
  RCUC changes required. If generators bid at additional gate openings then the ability to handle more than one price per trading day will be required as a minimum change
Impact Assessment of Option Group 1
Notes: <number>

## Slide 19
Compliance
  Option has been designated compliant
Discrimination
  Assumed that all Generation can re-bid in impact assessment so not an issue
Renewable interaction
  Assumed that additional forecasts will be made available
Impact Assessment of Option Group 1
Notes: <number>

## Slide 20
Six gate closures per day
All the security considerations of option 1 apply to option 2
Option 1 has been found to be complex and will present a major change and challenge for the SOs. Option 2 presents another degree of change.
With the pool based market arrangement, unit commitment decisions are fundamental to the secure and economic operation of the all island system.
Unit commitment runs with RCUC cannot be run every four hours (less than four hours available because the market engine need to complete prior to RCUC to provide interconnector flows)
Option 2 would require fundamental changes in SEM design
Impact Assessment of Option Group 2

## Slide 21: Conclusions
2 additional gate closures could be accommodated:
  Appropriate mitigation measures are required to reduce risks to system security
6 additional gate closures represent a significant change and would require:
  Major changes/replacement of RCUC
  Fundamental changes to SEM