## Slide 1
Mod_18_10 Intra Day Trading Working Group 7
  SO Impact Assessment

## Slide 2
Security Issues

## Slide 3: Security Issues – Some Facts
 | Ireland |  | GB | 
Max. Demand | 6,700 MW |  | 60,000 MW | 
Installed Wind | 3,100 | 46% | 10,000 | 17%
Interconnector Capacity | 1000 MW | 15% | 4,000 MW | 7%
Largest Generation Infeed | 445 MW | 7% | 1,320 MW | 2%
Comparison of forecast system capacities in 2013/14:

## Slide 4: Security Issues – Some Facts
Relative to other power systems, the all Island power system:
  has large generation unit sizes,
  has a high level of variable wind penetration which will grow further,
  will have significant external interconnection capacity.
These factors increase the criticality of unit commitment decisions:
  over committing will lead to an increase in constraint costs
  under committing will lead to load shedding.

## Slide 5: Security Issues - Potential Interconnector Flow Changes
Moyle Interconnector capacity at present is restricted to 450 MW import to 80 MW export with a rate of change limit of 300 MW/Trading Period (10 MW/min).
  Represents a potential 530 MW swing in < 1 hour.
Post EWIC, Interconnector capacity will be to 950 MW import to 580 MW export (assuming application of same 10 MW/min loading restriction).
  Represents a possible 1530 MW swing in < 2.6 hours.
If Moyle capacity increases to +/- 500 MW the flow limits become -1000 / +1000 MW (assuming application of same 10 MW/min loading restriction).
  Represents a possible 2000 MW swing in < 3.4 hours.

## Slide 6: Security Issues - Generator Notice Times and Gate Closure
The notice time required to synchronise a generator and get it up to minimum load can be up to 18 hours.
The market software does not take into account these notice times and will transition a unit from zero to minimum load in one trading period.
As gate closure and setting of the Moyle schedule occur approximately 18 hours before the start of the trading day, unit commitment decisions can currently be managed by the TSO's to minimise any security issues although constraint costs do arise.
Additional market gate openings between D-1, the start of the trading day and within the trading day will result in shorter notice time for plant commitment changes.
In summary - interconnector flows will be scheduled with plant that is not available in the time frames

## Slide 7: Security Issues - Generator Notice Times and Gate Closure
Chart: Time from Notification to Min Gen
| 3.9682539682539753E-4 | 3.9682539682539753E-4 | 3.9682539682539753E-4 | 3.9682539682539753E-4 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.24488333333333356 | 0.24488333333333356 | 0.33000000000000046 | 0.34000000000000036 | 0.34000000000000036 | 0.34000000000000036 | 0.34000000000000036 | 0.36333333333333334 | 0.36333333333333334 | 0.36333333333333334 | 0.60714285714285765 | 2.0902777777777808 | 2.0902777777777808 | 3.6770833333333335 | 4.5352333333333412 | 4.5352333333333412 | 6.5652243589743575 | 6.9166666666666714 | 6.9166666666666714 | 7.9070707070707069 | 8.7285714285714064 | 8.9016666666666708 | 8.9016666666666708 | 10.060606060606075 | 10.060606060606075 | 10.240320512820503 | 10.243819703759018 | 10.5 | 11.511111111111097 | 11.511111111111097 | 11.862382064001556 | 11.865555555555574 | 12.276041666666666 | 13.105659281758086 | 13.105659281758086 | 13.834271758103101 | 14.018248175182469 | 14.629533678756477 | 14.893643770749849 | 14.944551282051281 | 15.210256410256411 | 17.749816849816849 | 17.749816849816849 | 17.749816849816849 | 19.973777777777759
COLD - Notification to Min Gen | 73 | 146 | 219 | 292 | 321 | 350 | 408 | 466 | 519 | 560.61 | 602.22 | 706.22 | 758.22 | 810.22 | 862.22 | 914.22 | 1009.22 | 1104.22 | 1199.22 | 1311.22 | 1394.22 | 1477.22 | 1640.22 | 1694.22 | 1748.22 | 2152.22 | 2266.72 | 2381.22 | 2796.22 | 3259.22 | 3308.22 | 3362.22 | 3600.22 | 3838.22 | 4078.92 | 4319.62 | 4420.62 | 4667.62 | 4914.62 | 5015.62 | 5440.62 | 5558.19 | 5728.19 | 5898.19 | 6329.79 | 6420.79 | 6678.79 | 7123.79 | 7535.79 | 7887.79 | 8172.79 | 8457.79 | 8742.79 | 8879.79
WARM - Notification to Min Gen | 73 | 146 | 219 | 292 | 321 | 350 | 408 | 466 | 519 | 560.61 | 602.22 | 706.22 | 758.22 | 810.22 | 862.22 | 914.22 | 1009.22 | 1104.22 | 1199.22 | 1311.22 | 1394.22 | 1477.22 | 1640.22 | 1741.22 | 1979.22 | 2217.22 | 2271.22 | 2325.22 | 2572.22 | 2819.22 | 3223.22 | 3648.22 | 3762.72 | 3877.22 | 3994.79 | 4043.79 | 4097.79 | 4512.79 | 4613.79 | 4783.79 | 4953.79 | 5305.79 | 5750.79 | 6162.79 | 6625.79 | 6866.49 | 7107.19 | 7365.19 | 7796.79 | 8081.79 | 8366.79 | 8651.79 | 8788.79 | 8879.79
HOT - Notification to Min Gen | 73 | 146 | 219 | 292 | 321 | 350 | 408 | 466 | 519 | 560.61 | 602.22 | 706.22 | 758.22 | 810.22 | 862.22 | 914.22 | 1009.22 | 1104.22 | 1199.22 | 1311.22 | 1394.22 | 1477.22 | 1715.22 | 1953.22 | 2116.22 | 2233.79 | 2287.79 | 2341.79 | 2745.79 | 2794.79 | 2848.79 | 2949.79 | 3050.79 | 3297.79 | 3544.79 | 3959.79 | 4074.29 | 4188.79 | 4613.79 | 4783.79 | 4953.79 | 5211.79 | 5643.39 | 5884.09 | 6124.79 | 6569.79 | 6921.79 | 7333.79 | 7796.79 | 8081.79 | 8366.79 | 8651.79 | 8788.79 | 8879.79

## Slide 8: Security Issues – Impacts
The system generation requirement to meet a possible 1530 MW interconnector flow change with increasing system load and decreasing wind generation describes a boundary for security consideration.
Market schedules that are prepared closer to real time may not be physically realisable as plant which has to be run up from cold or warm may not be available in time – this could result in insufficient generation to meet demand and exports.
The magnitude of potential interconnector flow changes from export to import will require plant to be de-synchronised, this situation also requires consideration in terms of plant minimum on times, minimum down times (for re-synchronising when required) and two shifting limitations.
Currently, under extreme situations where NI generation is capacity limited, the N/S tie-line is constrained and SO-SO trades are unavailable due to GB generation unavailability, SONI could be required to load shed customers and maintain an export to GB.

## Slide 9: Security Issues – Summary
The magnitude and rate of interconnector flow changes coupled with a reduction in the time available to schedule plant has the potential to adversely affect system security.
Tools need to be developed to ensure system security is maintained.
The less exact and complex the UUC modelling is the more the constraint costs will be.

## Slide 10
Security Options

## Slide 11: Security – options
The following possible Security options could be adopted to manage security issues:
  1. Market scheduling
    The market scheduling engine modified to reflect generator parameters more accurately
      Generation plant notice times
      Generation run up characteristics
      Optimisation start boundary and optimisation time period needs to be considered.

## Slide 12: Security – Options
  2. Interconnector ramp rates
    The introduction of another interconnector requires consideration of ramp rate limits for normal operation and as a security mitigation control to limit excessive TP to TP changes.
    The reduction of the interconnector ramp rates to mitigate security issues would reduce the ramp rate to very small values which would restrict trading during normal operation.
  3. ATC changes
    A reduction in transfer capacity applied for security reasons in a similar manner to the GB / French interconnector rules. Rules will have to be agreed with NGC around which interconnector is to be constrained.
  4. Generator Flexibility Incentives
    e.g. introduce ‘warming’ contracts to shorten notice times
    CCGTs operating in Open cycle mode.
  5. SO-SO trades (already in place but not always available)

## Slide 13
    Security
    Control the issue by producing market interconnector schedules that can be physically accommodated without compromising system security.
    Allow alteration of the schedule by the SO to maintain security. Prior to altering an interconnector scheduled flow the SO would, after normal plant scheduling, trade out of the situation (potentially including trading with capacity holders), if trades are not available then the transfer would be restricted either by an ATC reduction or dispatch constraint.

## Slide 14
Example of Market and RCUC run timings assuming:
Both Generation and Interconnector users will bid at gate openings
RCUC (and UUC) can handle more than one price per trading day
The market produces an interconnector schedule that does not require alteration for security.

## Slide 15
Example of Gate Closure and RCUC Run Timings
SEM EA1
Gate
Closure
09:30
11:00
06:00
11:30
06:00
06:00
13:00
06:00
SEM EA2
Gate
Closure
16:00
TD-1
TD
13:00
Publish EA1 Market Schedule
Day Ahead
RCUC
Run
Day Ahead
RCUC
published
SEM WD1 Gate Closure
08:00
09:30
Publish EA2 Market Schedule
Publish WD1 Market Schedule
09:30
12:30
Publish Operations Schedule
Within Day RCUC Gate Closure