## Slide 1: Demand Side Unit Workshop 9 December 2010 Yvonne Coughlan
www.eirgrid.com

## Slide 2: Current Demand Side Activity
Nightsaver & Economy 7 schemes
SEM – opportunity for Demand Side units (DSU) and Aggregated Generator Units (AGU)
System Operator Schemes
  WPDRS
  Powersave
  STAR (interruptible load)
ESB WDRI Scheme
Home energy savings schemes
www.eirgrid.com
Notes: Identified WPDRS as a potential barrier to take up of demand side in SEM.
<number>

## Slide 3: Key TSO Workstreams for DSU
Grid Code
  Requirements for DSU
  Compliance Testing/Commissioning
  Compliance with dispatch instructions
NCC Communications
  SCADA
  Control Facility
Performance Monitoring
  TSO Validation of performance of DSU
www.eirgrid.com

## Slide 4: Grid Code
www.eirgrid.com

## Slide 5: Grid Code - Current Requirements Planning Data (PCA5)
Name of Demand Side Unit;
Location of Demand Site(s);
The name of the Transmission Station(s) to which the Demand Site(s) is/are normally connected;
Total Demand Reduction Capability (MW);
Demand Reduction Capability available from on-site Generation (MW);
Demand Reduction Capability available from avoided Demand consumption (MW);
Annual Demand Profile.
(Also per individual demand site)
www.eirgrid.com

## Slide 6: Grid Code Other Requirements (PC5.2) Planning Data
Following comparison with arrangements in Northern Ireland
  MPRN Identifier
  Electrical configuration of demand sites
  Metering details and metering configuration
  Number of starts per annum
  Confirmation of DSO permissions to operate
  Reconfiguration at SO request for system security reasons
www.eirgrid.com

## Slide 7: Grid Code Other Requirements
Initial Demand Reduction Time (Time to be defined in connection conditions)
Demand Profile (needs to be investigated further)
Max Ramp up rate /Max Ramp down rate
Maximum down time
Minimum down time
www.eirgrid.com

## Slide 8: Grid Code Connection Conditions (CC7.4)
Each Demand Side Unit shall, as a minimum, have the following capabilities:
  Able to provide Demand Reduction between 0 MW and the Demand Reduction Capability;
  Max Ramp Up Rate not less than 1.5% of Demand Reduction Capability per minute
  Max Ramp Down Rate not less than 1.5% of Demand Reduction Capability per minute
  Minimum Down-Time not greater than 30 minutes for Demand Side Units; and
  Maximum Down- Time not less than 2 hours for Demand Side Units.
Each Demand Side Unit with on-site Generation, shall have the following capabilities:
  operate continuously at normal rated output at Transmission System Frequencies in the range 49.5Hz to 50.5Hz;
  remain synchronised to the Transmission System at Transmission System Frequencies within the range 47.5Hz to 52.0Hz for a duration of 60 minutes;
  remain synchronised to the Transmission System at Transmission System Frequencies within the range 47.0Hz to 47.5Hz for a duration of 20 seconds required each time the Frequency is below 47.5Hz; and
  remain synchronised to the Transmission System during a rate of change of Transmission System Frequency of values up to and including 0.5 Hz per second.
www.eirgrid.com

## Slide 9: Grid Code Compliance Testing/Commissioning a DSU
Start time from initial dispatch instruction to start (Initial demand reduction time)
MW output (dispatched versus SCADA)
Time from dispatch instruction to shut down to actual shutdown
Monitoring of meter data against dispatch instructions
Testing of signals from individual demand sites to aggregated site
Need to develop Commissioning Procedure
www.eirgrid.com

## Slide 10: Grid Code Compliance with Dispatch Instructions
If the Dispatchable Demand customer is deemed by the TSO to be non compliant with three dispatch instructions (OC10.7.1.8)
  the TSO shall notify the Dispatchable Demand Customer of the non-compliance
  the Dispatchable Demand Customer should take immediate action to remedy such non compliance.
  The TSO has the right to instruct the Market Operator that the Demand Side Unit is in breach of the Grid Code. In such cases the TSO may set the Demand Side Unit’s Availability to zero until Testing is completed on compliance with Dispatch Instructions.
www.eirgrid.com

## Slide 11: Communications
www.eirgrid.com

## Slide 12: Communications – SCADA (OC12.2)
For Dispatchable Demand Customers, SCADA remote terminal equipment shall also be required at the Control Facility for the transmission of signals and indications to and from the NCC. (OC7.2.5.3.2)
Dispatchable Demand Customers and Generator Aggregators shall provide the TSO the specification of the method of aggregation of SCADA from multiple sites. The minimum specifications shall be agreed with the TSO in advance.
For a Demand Side Unit or Aggregated Demand Side Unit which achieves the Demand Reduction only by operating a Generator or Generators, the Demand Side Unit or the Aggregated Demand Side Unit shall be deemed compliant if the SCADA signal confirms that the increased output of the generation is within 5% of the Demand Reduction.
Installation of SCADA - RTU, Power, GPS clock etc. Lead time: 6 – 8 months
Review of signals required will be carried out
www.eirgrid.com

## Slide 13: Communications – Control Facility (OC7.2.4.3.6)
For Dispatchable Demand Customers, the Control Facility shall be staffed by a Responsible Operator who shall respond to communications from the TSO without undue delay
  to accept and execute Dispatch Instructions;
  to receive and acknowledge receipt of requests, for amongst other matters, operation outside the Declared values of Demand Reduction.
The Responsible Manager shall be authorised by the Dispatchable Demand Customer to perform the following functions on behalf of the Dispatchable Demand Customer:
  to make estimates in accordance with Good Industry Practice as to the Demand Reduction;
  to make Declarations of the Demand Reduction for each Dispatchable Demand Customer; and
  to communicate with respect to issues regarding Outages of each [DSU].
www.eirgrid.com

## Slide 14: Performance Monitoring
www.eirgrid.com

## Slide 15: Performance Monitoring (OC10.4.5.2)
DSU performance will be performed by the TSO on a needs-be basis: (OC
For a Demand Side Unit or Aggregated Demand Side Unit which achieves the Demand Reduction only by reducing their Demand
  Demand Profile = Metered Demand + Demand Reduction +/- 5 % (Compliant)
For a Demand Side Unit or Aggregated Demand Side Unit which achieves the Demand Reduction by reducing their Demand and operating a generator or generators
  Demand Profile = Metered Demand + Demand Reduction +/- 5 % (Compliant)
For Demand Side Units which are not Dispatched but have been declared Available in an Availability Notice,
  Demand Profile – Metered Demand = +/- 5 % (Compliant)
www.eirgrid.com

## Slide 16: Performance Monitoring
EirGrid will request access to the individual demand site meters from MRSO
EirGrid will poll the demand site meters that form part of the DSU
EirGrid will aggregate the individual demand site meters to form the DSU
EirGrid will then validate the metered data information against the dispatch instructions issued by NCC
www.eirgrid.com

## Slide 17: Next Steps
Drafting TSO Application form by EirGrid
Completion of TSO Application form by DSU
Kick off process for RTU installation
Request for meter data from MRSO
Develop Grid Code Compliance Testing
EDIL Setup
www.eirgrid.com